## Local Proc (hidden)
No II | Solar Water Pumping incl. Control unit & accessories | Specification | Unit | Qty, To procure | Estimated Cost / pcs | Estimated Total cost
6 | cable clips | Grundfos,fastening of cable and straining wire to the riser pipe Product No: 115016 Or equivalent | set | 4 | 100 | 400

## Lot 1 - Project I_Spec 160 kWp
Photovoltaic System - Location: Al Dakla Oasis - Egypt
Specification: Grid-connected photovoltaic system with ground mounted string inverters Solar generator: Polycrystalline solar modules (peak power 160 Wp) mounted on a greenfield racking system with an inclination angle of 15° - 20°.
Pos. | Technical Specification - Photovoltaic Solar Plant 160 kWp |  | Qty | Remarks Comperative specification should indicate any deviation from techn. Parameter or functional description of tender specification. If there is no deviation to the specification on the left side please state "Yes" or "ü"; further particularities | Unit Price | Total Price
0 | PRODUCTS DOCUMENTATION AND SPECIFICATION
For each product offered the following documentation has to be included:
0.1 | Product description and data sheets
0.2 | Installation instructions
0.3 | Connection plans
0.4 | Commissioning instructions
0.5 | Operating instructions
0.6 | Maintenance instructions
0.7 | Error sources, error diagnosis and troubleshooting instructions
1 | PHOTOVOLTAIC SOLAR MODULES - TOTAL POWER 160 kWp
1.1 | Polycrystalline solar modules, power of single module > 295 Wp - STC |  | 542
1.2 | Weather resistant Junction box with 3 Bypass-diodes, protection class IP 67 in accordance with IEC 62790
1.3 | Wiring of the modules with pin-and-socket connector in accordance with IEC 62852, IP68 when connected (MC4 connectors)
1.4 | Temperature coefficient Pmpp: | <-0,40 %/°C
1.5 | Temperature coefficient Voc: | <-0,33%/°C
1.6 | Temperature coefficient Isc: | >0.02 %/°C
1.7 | Operating temperature range: | -40…+85°C
1.8 | NOCT | 45°C (+/- 2°C)
1.9 | Module efficiency | > 16.0%
1.10 | Positive power sorting
1.11 | PID free in accordance with IEC62804
1.12 | Min. 20 year product warranty
1.13 | 25 year linear power output warranty, max. performance degression of 0.7% p.a. from 97.5% in year 1
1.14 | CE- conformity, TUV quality certification
1.15 | Horizontal and vertical assembly possible
1.16 | Max. system voltage 1000V
1.17 | Mechanical load (acc. IEC 61215 (5400Pa superimposed load and 2400Pa suction load))
1.18 | Nominal power min. 295 Wp at IEC-Conditions (radiation 1000W/m²,Air-Mass 1.5, 25°C)
1.19 | Modules certified according to IEC 61215:2016, IEC61730:2016, IEC 61701, IEC 61716, IEC 60068-2-68
1.20 | Manufactured in accordance with DIN EN ISO 9001:2015 and 14001:2015
1.21 | Manufactured in accordance with OHSAS 18001:2007
1.22 | Flasher records from the manufacturer of the modules which indicates actual power output per serial number have to be provided within ten days after shipment/delivery
1.23 | Documentation: | English
2 | SOLAR MOUNTING SYSTEM for 160 kWp Solar Plant - Greenfield Racking System |  | 1
2.1 | Greenfield mounting system for framed PV modules (floor mounting system)
2.2 | Module format: | 4 modules horizontally one above the other, 12 module side by side per table
2.3 | Rear and front post aluminium bolted to steel sigma profiles | Connecting elements, solar panel clamps (fasteners)
2.4 | Material: Complete assembly material must be included (stainless steel, aluminium) | Aluminum and stainless steel
2.5 | Mounting inclination angle | 17° to 20°
2.6 | Posts (support): sigma profiles made of galvanised steel for embedding in concrete blocks | Concrete blocks will be produced on site
2.7 | Integrated cable channels (ducts)
2.8 | Product warranty | 10 years
3 | 3 Phase Solar String Inverter - transformerless |  | 3
3.1. | Input
3.1.1 | Max. generator power | 75000 Wp STC
3.1.2 | Max. input voltage | 1000 V
3.1.3 | MPP voltage range / rated input voltage | 500 V - 800 V / 670 V
3.1.4 | Min. input voltage / start input voltage | 150 V / 188 V
3.1.5 | Max. operarting input current / per MPPT | 120 A / 20 A
3.1.6 | Max. short circuit current per MPPT / per string input | 30 A / 30 A
3.1.7 | Number of independent MPPT inputs / strings per MPPT input | 6 / 2
3.2 | Output
3.2.1 | Rated power at 230 V- 50 Hz | 50000 W
3.2.2 | Max. AC apparent power | 50000 VA
3.2.3 | AC nominal voltage (V) | 220 / 380 V; 230 V / 400 V; 240 V / 415 V
3.2.4 | AC voltage range (V) | 202 V - 305 V
3.2.5 | AC grid frequency / rang | 50 Hz (44Hz - 55Hz); 60 Hz (54 Hz - 65 Hz)
3.2.6 | Rated power frequency | 50 Hz / 230 V
3.2.7 | Max. output current / Rated output current | 72.5 A / 72.5 A
3.2.8 | Output phases / AC Connection | 3 / 3-(N)-PE
3.2.9 | Power factor at rated power | 1 / 0.0 leading to 0.0 lagging
3.2.10 | THD | < 3%
3.3 | Efficiency
3.3.1 | Max. efficiency / European Efficiency | 98.1% / 97.8%
3.4 | General information
3.4.1 | Operating temperature range | -25 … + 60°C
3.4.2 | Noise emission (typical) | < 65 dB(A)
3.4.3 | Topology | transformerless
3.4.4 | Degree of protection (as per IEC 60529) | IP65
3.4.5 | Climatic category (accordding to IEC 60721-3-4) | 4K4H
3.4.6 | Max. permissible value for relative humidity (non condensing) | 100%
3.4.7 | Mounting | ground mounted on mounting feet
3.4.8 | DC / AC connection | PV connectors / screw terminals
3.4.9 | LED indicators (status / fault / communication)
3.4.10 | Interfaces: Ethernet / WLAN / RS485
3.4.11 | Data interface | Modbus, Speedwire, Webconnect
3.4.12 | Multi-Function relay
3.4.13 | Integrated plant control
3.4.14 | Off-grid capable
3.5. | Certificates | ANRE 30, AS 4777, BDEW 2008, C10/11:2012, CE, CEI 0-16, CEI 0-21, EN 50438:2013*, G59/3, IEC 60068-2-x, IEC 61727, IEC 62109-1/2, IEC 62116, MEA 2016, NBR 16149, NEN EN 50438, NRS 097-2-1, PEA 2016, PPC, RD 1699/413, RD 661/2007, Res. n°7:2013, SI4777, TOR D4, TR 3.2.2, UTE C15-712-1, VDE 0126-1-1, VDE-ARN 4105, VFR 2014, P.O.12.3, NTCO-NTCyS, GC 8.9H, PR20, DEWA
3.6 | Protective devices
3.6.1 |  | Disconnecting device - input side
3.6.2 |  | Ground fault monitor
3.6.3 |  | DC-reverse polarity protections
3.6.4 |  | AC-short-circuit current capability / galvanically isolated
3.6.5 | DC-Overvoltage Protection | Built in DC-Overvoltage protection Typ II
3.6.6 | AC-Overvoltage Protection | Built in AC-Overvoltage protection Typ II
3.6.7 |  | All-pole sensitive residual-current monitoring unit
3.6.8 | Protection class (according to IEC 62109-1) Overvoltage category (according to IEC 62109-1)
3.6.9 | Universal mounting system for all inverters (floor mounting)
3.7 | Warranty | min 5 years (extendable)
3.8 | Documentation | English
4 | AC Distribution cabinet with current transducer measurement 160 kVA |  | 1
4.1 | 4-pole Busbar Current Distribution System 400 A (TT-Grid) | Metering cabinet according to the standards of the electric utility with terminals, fuses, cabling, data plug socket, cooper busbars and V-type terminals.
4.2 | 1 x NH3 - NH fuse switch disconnector - Utility | V-type terminals - Clamping area: 10 - 240 mm², 3 x 1pol
4.3 | 1 x Instruments transformer kit 170x30x10mm | Instrument transformer to be provided by Power Provider
4.4 | 1 x NH2 - NH fuse switch disconnector - Loads | V-type terminals- Clamping area: 10 - 240 mm², 3 x 1pol
4.5 | Main circuit breaker | 400 A max 4-pole, electric actuator
4.6 | External system protection | Bender LINETRAXX VMD460-NA
4.7 | 3 x NH2 fuse switch disconnector - Photovoltaic System | V-type terminals - Clamping area: 10 - 240 mm²
4.8 | Mounting area 450mm for 3-point current transducer meter
4.9 | DO 1/3 Line fuses
4.10 | Internal fan with filter
4.11 | Protective cover
4.12 | Cable clamp rail
4.13 | Degree of protection (as per IEC 60529) | IP44
4.14 | weatherproof, UV-resistant, resistant to chemicals
4.15 | Class of protection II (with electrical insulation)
4.2 | Enclosure: | fibreglass-reinforced polyesters (using the SMC process), IEC-695-2-1, halogen-free
colour: grey, similar to RAL 7035
4.3 | Dimensions: | Height: 1370 mm; sockel 950 mm
Width: 1465 mm
Depth: 470 mm
4.4 | Certificates | VDE (German Association for Electrical, Electronic and Information Technologies) 0660 Sect. 500 / IEC 439-1
In compliance with DIN 43870, Guideline 07/04 VdN (Association of Network Operators)
5 | ACCESSORIES
5.1 | PV Plant controller / Data manager
6 | SOLAR CABLE
6.1 | 1 x 6mm², fine copper cable | TÜV Approval Nr. TÜV 2 PfG 1169/08.2007 or equivalent Ozone Resistant according to EN 50396 or equivalent Flame Retardant according to IEC/EN 60332-1-2 or equivalent UV Resistant according to HD 605/A1 or equivalent Halogen Free according to EN 50267-2-1, EN 60684-2 or equivalent Cold Resistant according to IEC/EN 60811-1-4 or equivalent Low Smoke according to IEC/EN 61034 or equivalent Acid and Alkaline Resistant according to IEC/EN 60811-2-1 or equivalent Low Corrosivity of gases according to EN 50267-2-2 or equivalent Weather Resistant according to HD 605/A1 or equivalent Low toxicity of gases according to EN 50267-2-1 or equivalent | 2000 m
7 | SOLAR CABLE CONNECTORS set (m/f) |  | 100
7.1 | Solar Connector, 4-6mm², min 30A/1000V, Spring Closure Construction (tool free crimping) polarity: Minus |  | 50
7.2 | Solar Connector, 4-6mm², min 30A/1000V, Spring Closure Construction (tool free crimping) polarity: Plus |  | 50
8 | Installation material
8.1 | Grounding rods, galvanized steel, 1,50 m; with cable connector |  | 2
8.2 | Solar wire management (solar cable clips) | Button head mounts with cable ties (UV-resistant) | 1200
8.3 | Cable ties (black), outdoor use (UV-resistant!) | 4,6 x 300 mm | 1000
8.4 | Cable ties (black), outdoor use (UV-resistant!) | 7,6 x 460 mm | 1000
8.5 | Equipontential bonding rail |  | 1
9. | Installation according to local and international norms and codes | 1
9.1 | Installation of the complete system under local conditions
9.2 | Connection and embedding to the local infrastructure
10. | Documentation of the entire system | 1
10.1 | Network wiring diagram for the monitoring system
10.2 | Product descriptions and datasheets for all equipment
10.3 | Single-Line Diagram for the complete system
10.4 | Product manufacturer warranties
10.5 | Installation guide in English
10.6 | User manual in English
10.7 | Service notes in English
10.8 | Fault analysis and troubleshooting in English
10.9 | Data sheets for all components in Englisch
11. | General Confirmations & Documentation | 1
11.1 | At least three years experience with the delivery and installation of goods similar to the requested system
11.2 | At least three contracts of a size comparable to the present contract during the last three years
11.3 | Annual tunrnover not less than EURO 1.5 million/annum for PV-Systems during the last three years
11.4 | ISO 9001 certification of the vendor
11.5 | Site survey
11.6 | System to install will perform according to the required output and system components are ensured to function togehter
11.7 | Scope of supply contains all material for the installation and commissioning of the system
11.8 | Local Partner: specify adress + references; licensed with District Electricity Co.
12. | Transport | 1
12.1 | Incoterm 2010 - DDP Balat / Dakhla - Egypt | 25°33'45.29" - 29°15' 51.48"

## Lot 1 - Project II_Spec 7 kWp
Photovoltaic System - Location: Al Dakla Oasis - Egypt
Specification: PV Off-Grid system (1 ph) with backup functionality - DC-coupled technology (MPPT solar controllers); single phase battery inverter Solar generator: Polycrystalline solar modules (peak power 7 kWp) mounted on a greenfield racking system with an inclination angle of 15° - 20°. Batteries: Min. 54KWh (C10), OPzV 2V cells, resistant to cycling: min. 1500 cycles at DoD 80 %.
Pos. | Technical Specification - 7 kWp - Off-Grid System |  | Qty | Remarks Comperative specification should indicate any deviation from techn. Parameter or functional description of tender specification. If there is no deviation to the specification on the left side please state "Yes" or "ü"; further particularities | Unit Price | Total Price
0 | PRODUCTS DOCUMENTATION AND SPECIFICATION
For each product offered the following documentation has to be included:
0.1 | Product description and data sheets
0.2 | Installation instructions
0.3 | Connection plans
0.4 | Commissioning instructions
0.5 | Operating instructions
0.6 | Maintenance instructions
0.7 | Error sources, error diagnosis and troubleshooting instructions
1 | PHOTOVOLTAIC SOLAR MODULES - TOTAL POWER 7 kWp |  | 1
1.1 | Mono/polycrystalline solar modules, power of single module > 295 Wp |  | 24
1.2 | Module description: technical specifications - Document which certifies that the modules production process is subject to a permanent quality control
1.3 | Weather resistant Junction box with 3 Bypass-diodes on the backside of the modules with protection class IP 67
1.4 | Wiring of the modules with pin-and-socket connector according to EN 50521 or equivalent
1.5 | Temperature coefficient Pmpp: | <-0,43 %/°C
1.6 | Temperature coefficient Voc: | <-0,33%/°C
1.7 | Temperature coefficient Isc: | >0.02 %/°C
1.8 | Operating temperature range: | -40…+85°C
1.9 | NOCT | 45°C (+/- 2°C)
1.10 | Module efficiency | > 14.0%
1.11 | Positive power sorting
1.12 | Min. 10 year product warranty
1.13 | 25 years linear performance guarantee for the PV modules, such that in year one the guaranteed output power is at least 97% of the nominal power and in year 25 equal or above 80%.
1.14 | CE- conformity, TUV quality certification
1.15 | Horizontal and vertical assembly possible
1.16 | Max. system voltage 1000V
1.17 | Mechanical load (acc. IEC 61215 (5400Pa superimposed load and 2400Pa suction load))
1.18 | Pre-cabled with solar connectors (min. IP 65), connector type: locable, weather proof, plug and play connector
1.19 | Nominal power min. 295 Wp at IEC-Conditions (radiation 1000W/m²,Air-Mass 1.5, 25°C)
1.20 | Nominal ground coverage>134 Wp/m2 at IEC-conditions
1.21 | Product certification | IEC 61215 (Ed.2)
1.22 | Protection class II/ IEC 61730
1.23 | Documentation: | English - French
1.24 | Test standards according to: IEC 61215 (crystalline silicon performance)
2 | SOLAR MOUNTING SYSTEM for 7 kWp (= 24 solar modules) Solar Plant - Greenfield racking system |  | 1
2.1 | Greenfield Racking System (floor mounting system); Variable mounting angle for module table rails 15° or 20° | Individual mounting of 12 solar modules on a separate substructure in two rows
2.3 | Mounting rail MLC 86 x 60, 4,25 m length EN AW 6063 T66
2.4 | Rectangular Pipe 67 x 44,6 mm, length: 490 mm, rail connector
2.5 | Single pole steel root set S235 for extra solid TR foundations, with variable mounting angle for module table rails, hot dip zinked acc. to DIN EN ISO 1461 | Prefabricated foundation,direct bury foundation (e.g. ground plates fabricated from steel profiles)
2.6 | Complete assembly material must be included (stainless steel, aluminium) | Connecting elements, solar panel clamps (fasteners)
3 | MPPT SOLAR CONTROLLER with two separate solar generator inputs |  | 1
3.1 | Input 1
3.1.1 | Max. solar power at STC | 3500
3.1.2 | Max. current | 13 A
3.1.3 | MPP voltage range | 250-500 V
3.1.4 | Maximum solar open circuit voltage | 600 V
3.1.5 | Minimum solar functional circuit voltage | 200 V
3.1.6 | Recommended MPPT voltage | 250 - 500
3.1.7 | Electrical characteristics battery side
3.1.8 | Maximum output current | 60
3.1.9 | Nominal battery voltage | 48 V
3.1.10 | Operating voltage range | 36 - 68 V
3.1.11 | Battery grounding possibility | Battery + or battery -
3.2 | Input 2
3.2.1 | Max. solar power at STC | 3500
3.2.2 | Max. current | 13 A
3.2.3 | MPP voltage range | 250-500 V
3.2.4 | Maximum solar open circuit voltage | 600 V
3.2.5 | Minimum solar functional circuit voltage | 200 V
3.2.6 | Recommended MPPT voltage | 250 - 500
3.3 | Electrical characteristics battery side
3.3.1 | Maximum output current | 60
3.3.2 | Nominal battery voltage | 48 V
3.3.3 | Operating voltage range | 36 - 68 V
3.3.4 | Battery grounding possibility | Battery + or battery -
3.4 | Efficiency
3.4.1 | Max. efficiency | >98 %
3.4.2 | MPPT efficiency | > 99,8 %
3.4.3 | Maximum stand-by self consumption 48 V | < 25 mA (1,25 W)
3.5 | General information
3.5.1 | Charging stages | 4 stages: Bulk, Absorption, Float, Equalization
3.5.2 | Battery temperature compensation (with accessory) | -3 mV/°C/cell (25°C ref) default value adjustable -8 to 0 mV/°C
3.5.3 | Communication | remote control & communication - internal bus
3.5.4 | Protection against reverse polarity | •
3.5.5 | Protection against battery overvoltage | Up to max. 80 V
3.5.6 | Ground fault protection | Programmable
3.5.7 | Protection against over temperatur | •
3.5.8 | Protection against reverse current at night | •
3.5.9 | Galvanic isolation | •
3.5.10 | Solar generator connection (6 mm²) | locable, weather proof, plug and play connector, tool free
3.5.11 | Battery connection 2 x 50 mm² / M10
3.5.12 | Protection index | IP20
3.5.13 | EU declaration of conformity | EU: EN 62109-1:2010 - EMC Directive 2014/30 EU: EN 61000-6-2:2005 EN 61000-6-4:2007/A1:2011
3.5.14 | ISO Certification | 9001:2008 /14001:2004
3.5.15 | Operating ambient temperature range | -20 to 55°C
3.5.16 | Humidity | 95% (non-condensating)
3.6 | Warranty | 5 years
3.7 | Documentation | English - French
4 | BATTERY INVERTER Off-GRID 8000 VA / 48 V |  | 1
4.1 | Bi-directional battery inverter capable to control and manage different input sources and charge and monitor battery banks
4.2 | Inverters parameters
4.2.1 | Output voltage | 230 V (+/- 2%)
4.2.2 | Output frequency (adjustable range) | 50 Hz (45Hz - 65Hz)
4.2.3 | Contimuos AC power output at 25°C | 7000 VA
4.2.4 | AC power output for 30 min / 5 sec. at 25°C | 8000 VA / 21 kVA
4.2.5 | Max. load | up to short-circuit
4.2.6 | Harmonic distortion | < 2 %
4.2.7 | Power factor (Cos f) | 0,1 - 1
4.2.8 | Sinus modulation | Pure sine wave
4.2.9 | Max. efficiency | >95 %
4.2.10 | Self- consumption OFF/Stand-by/On | 1,8 / 2,4 / 30 W
4.3 | Generator input voltage parameters
4.3.1 | Nominal generator input voltage (range) | 230 V / ( 150 - 265 Vac)
4.3.2 | Input frequency (range) | 45 Hz - 65 Hz
4.3.3 | Maximum generator input current (transfer relay) | 50 A
4.4 | Battery Charger
4.4.1 | Nominal battery voltage (range) | 38 - 60 V
4.4.2 | Charge characteristics | 6 steps:
4.4.3 | Maximum charging current | 120 A
4.4.4 | Temperature compensation | with accessory
4.4.5 | Power factor correction | EN 61000-3-2
4.5 | Physical data
4.5.2 | Cooling principle | Temperature controlled active cooling
4.5.3 | Protection Index | IP20
4.5.4 | Ambient working temperate range | -25 … +55°C
4.6 | Features
4.6.1 | Modular extendable | 1 and 3 phase operation
4.6.2 |  | Extendable up to 9 units (72 kVA)
4.6.3 |  | Compatible with AC coupling
4.6.4 |  | Automatic deep discharge protection
4.6.5 |  | Automatic overcharge protection
4.6.6 | Multifunction contact (programmable) | 2 independent contacts16 A ac / 5 A dc (potential-free change- over contact
4.6.7 | Generator management | Smart boost and active filtering
4.6.8 |  | Management and limitation ot AC sources
4.6.9 |  | Power shaving of the consumption peaks
4.6.10 |  | Transfer time 0 - 15 ms
4.6.11 | Automatic protection of sources against overload
4.6.12 | Overload and short circuit protection | Automatic disconnection with 3 time restart attempt
4.6.13 | Overheat protection | Warning bevor shut-off with automatic restart
4.6.14 | Acousitc level | < 40 dB / < 45 (without / with ventilation)
4.6.15 | Monitoring features | Visual operation indicators by LED/ Display
4.6.16 |  | RS-232 communication for remote supervision
4.6.17 | EU declaration of conformity | EU: EN 50178:1997 - EMC Directive 2014/30 EU: EN 62040-2:2006, EN 61000-3-2:2014 EN 61000-3-12:2011
4.6.18 | ISO Certification | 9001:2008 /14001:2004
4.7 | Warranty | 5 years
4.8 | Documentation | English - French
5 | ACCESSORIES
5.1 | Module for the measuring and calculating State of Charge (SoC) and battery temperature, 5 m cable |  | 1
5.2 | Remote control modul for the setting of parameters and for the display of values measured (with 2 m cable) |  | 1
5.3 | Communication modul |  | 1
5.4 | Smart-Energy meter, 3-phase, LAN + RS485 Port | Indirect measurement via current transducer | 1
5.5 | Patch-cable 2m - Cat6e |  | 2
6 | SOLAR BATTERY (48V system voltage) Valve Regulated Lead Acid - battery |  | 1
6.1 | OPzV SOLAR BATTERY, | Single 2 V VRLA stationary battery, electrolyte is fixed in form of gel | 24
6.2 | Min. nominal rating 2V/1100 Ah (min.) (C10) 20°C
6.3 | Live expectancy of up to 20 years, cycling expectancy greater than 1500 cycles at 80% depth of discharge at 20°C.
6.4 | Self discharge less than 4%/month at 25°C
6.5 | Suitable for ambient temperature 0°C to 50°C
6.6 | Int. Standards according to: IEC 60896-21-22, IEC 61427 or equivalent; EN 50272-2 or equivalent
6.7 | ISO Certification ISO 9001/14001
6.8 | Each battery must be labeled indicating at least: Manufacturer, type, model number, rated voltage and capacity C10 Manufacturing date of the batteries should be not older than 2 month.
6.9 | Incl. Pole screws with isolated bolt head and battery connectors + flexibel connector first to second row
6.10 | Battery rack for 24 OPzV batteries in two rows |  | 1
7 | BATTERY FUSE BOX |  | 1
7.1 | IP 65 - Wall mounted |  | 1
7.2 | Dual pole MCB-DC (or hydraulic-magnetic breaker) 125 A - 48 Vdc for MPPT-Controller
7.3 | Dual pole Hydraulic magnetic breaker 200 A - 48 Vdc for Battery Inverter
7.4 | 1x auxiliary voltage output (48 V) with 8A (fuse-protected)
7.5 | Input / Output Terminals M10
7.6 | Common battery connection - positive (bus bar +)
7.7 | Common battery connection - negative (bus bar -)
8 | BATTERY CONNECTION CABLE SETS - M10/M10; 150 cm
8.1 | Preconfigured cable set 2 x 1,5m - 70mm² (NSGAFÖU) M10 / terminal lugs - wire end ferrules |  | 2
8.2 | Preconfigured cable set 2 x 1,5m - 70mm² (NSGAFÖU) M8 / terminal lugs - wire end ferrules |  | 2
| Preconfigured cable set 1 x 0,5m - 70mm² (NSGAFÖU) M8 / M10 terminal lugs |  | 1
8.3 | Preconfigured cable set 2 x 1,5m - 50mm² (NSGAFÖU) M10 / M10 - terminal lugs - wire end ferrules |  | 2
8.4 | M10 cable lugs of the battery cables must fit through the cable glands of the battery inverter and MPPT-Controller!!
8.5 | Certification: CE
9 | SOLAR CABLE
9.1 | 1 x 6mm², fine copper cable for PV String connection to inverter, outdoor use, black [m] | TÜV Approval Nr. TÜV 2 PfG 1169/08.2007 or equivalent Ozone Resistant according to EN 50396 or equivalent Flame Retardant according to IEC/EN 60332-1-2 or equivalent UV Resistant according to HD 605/A1 or equivalent Halogen Free according to EN 50267-2-1, EN 60684-2 or equivalent Cold Resistant according to IEC/EN 60811-1-4 or equivalent Low Smoke according to IEC/EN 61034 or equivalent Acid and Alkaline Resistant according to IEC/EN 60811-2-1 or equivalent Low Corrosivity of gases according to EN 50267-2-2 or equivalent Weather Resistant according to HD 605/A1 or equivalent Low toxicity of gases according to EN 50267-2-1 or equivalent | 300
10 | SOLAR CABLE CONNECTORS |  | 30
10.1 | Solar Connector, 4-6mm², min 30A/1000V, Spring Closure Construction (tool free crimping) polarity: Minus |  | 15
10.2 | Solar Connector, 4-6mm², min 30A/1000V, Spring Closure Construction (tool free crimping) polarity: Plus |  | 15
11 | Tools
11.1 | Cordless hammer drill; 18V 3Ah with charger |  | 1
11.2 | Step drill - 8 - 20 mm |  | 2
11.3 | Set of torx drill bits (T10 - T40) |  | 2
11.4 | Set of stone drill bits in box from 5 mm - 10 mm |  | 1
11.5 | Set of metal drill bits in box from 1 mm - 13 mm |  | 1
12 | Installation material
12.1 | PV Connection box (fully assembled) for two individuell PV-strings with two-pole disconnect switch for each string (800 V / 35 A-dc) and SPD Typ II arrester 750 V-dc for each string; two separate output terminal blocks 6 - 10 mm² for each string; IP65 |  | 1
12.2 | AC main distribution cabinet (fully assembled): AC input MCB 50 A, surge protection SPD III, bypass switch, AC output MCB 50 A; RCD (30 mA), surge protection SPD III; loadshedding contactor 48 Vdc/ 230 V - 50 Aac; IP65 |  | 1
12.3 | Equipotential bonding rail |  | 2
12.4 | Grounding rods, galvanized steel, 1,25m; with cable connector |  | 2
12.5 | NYM - PE- 1 x 10 mm² / m |  | 25
12.6 | NYY-J 5 x 2,5 mm² / m |  | 250
12.7 | Flexible connection cable 2 x 2,5 mm² YSLY-OZ 2x2,5 VDE 0250, 0271, 0281, 0293; wire marking VDE 0293-3082 / m |  | 25
12.8 | Flexible AC connection cable, 3 x 10 mm²; YSLY-JZ 3X10; VDE 0250, 0271, 0281, 0293; wire marking VDE 0293-3082 / m |  | 25
12.9 | Flexible AC connection cable, 3 x 6 mm²; YSLY-JZ 3X10; VDE 0250, 0271, 0281, 0293; wire marking VDE 0293-3082 / m |  | 25
12.10 | Cable ties black 4,7 mm x 300 mm UV-resistant! |  | 300
12.11 | Corrugated pipe M32 for electrical installation, black / m |  | 100
12.12 | Mounting clips for corrugated pipe M32 |  | 100
12.13 | Cable ducts, PVC 60 x 110 mm, RAL9010 / m |  | 6
12.14 | Dowels / wall plucks 8 x 50 mm |  | 100
12.15 | Dowels / wall plucks 10 x 60 mm |  | 50
12.16 | Torx headed chipboard screw 5 x 70 mm |  | 250
12.17 | Torx headed chipboard screw 8 x 70 mm |  | 100
13 | LED Street Lamp (head only) |  | 10
13.1 | Beam angle | 120°
13.2 | Color Designation | White Light (WH)
13.3 | Correlated Color Temperature | 6000 K
13.4 | Energy Consumption | < 20 kWh /1000 h
13.5 | Energy Energy Efficiency Consumption | A+
13.6 | Flux | 2000 lm
13.7 | FLUX per watt | 100lm/W
13.8 | Input voltage | AC95-265V - 50 - 60 Hz
13.9 | Protection Index | IP65
13.10 | Life span | > 25 000 Hours
13.11 | Material | Aluminium
13.12 | Mercury Free
13.13 | On/Off Cycles | > 100 000x
13.14 | Power LED | 20 W
13.15 | Protection Class | II
13.16 | Temperature | -30°C - 50°C
13.17 | Warranty | 2 years
14 | Installation according to local and international norms and codes | 1
14.1 | Installation of the complete system under local conditions
14.2 | Connection and embedding to the local infrastructure
15 | Documentation of the entire system | 1
15.1 | Network wiring diagram for the monitoring system
15.2 | Product descriptions and datasheets for all equipment
15.3 | Single-Line Diagram for the complete system
15.4 | Product manufacturer warranties
15.5 | Installation guide in English
15.6 | User manual in English
15.7 | Service notes in English
15.8 | Fault analysis and troubleshooting in English
15.9 | Data sheets for all components in Englisch
16 | General Confirmations & Documentation | 1
16.1 | At least three years experience with the delivery and installation of goods similar to the requested system
16.2 | At least three contracts of a size comparable to the present contract during the last three years
16.3 | Annual tunrnover not less than EURO 1.5 million/annum for PV-Systems during the last three years
16.4 | ISO 9001 certification of the vendor
16.5 | Site survey
16.6 | System to install will perform according to the required output and system components are ensured to function togehter
16.7 | Scope of supply contains all material for the installation and commissioning of the system
16.8 | Local Partner: specify adress + references; licensed with District Electricity Co.
17 | Transport | 1
17.1 | Incoterm 2010 - DDP Balat / Dakhla - Egypt | 25°33'45.29" - 29°15' 51.48"