## Local Proc (hidden)
No II | Solar Water Pumping incl. Control unit & accessories | Specification | Unit | Qty, To procure | Estimated Cost / pcs | Estimated Total cost
6 | cable clips | Grundfos,fastening of cable and straining wire to the riser pipe Product No: 115016 Or equivalent | set | 4 | 100 | 400

## Lot 2 - Project I_Solar Pump
Solar Pump System- Location: Al Dakla Oasis - Egypt
Specification: Submersible pump with 3-phase motor (54 kW) driven by VFD (varibale frequency drive 55 kW) for agricultural irrigation (drip irrigation) Water supply from a deep well (dynamic head 65 m), required water volume 250 m³/h Solar generator: Polycrystalline solar modules (peak power 82 kWp) mounted on a greenfield racking system with an inclination angle of 15° - 20°.
Pos. | Technical Specification - Solar Pump System 82 kWp |  | Qty | Remarks Comperative specification should indicate any deviation from techn. Parameter or functional description of tender specification. If there is no deviation to the specification on the left side please state "Yes" or "ü"; further particularities | Unit Price | Total Price
0 | PRODUCTS DOCUMENTATION AND SPECIFICATION
For each product offered the following documentation has to be included:
0.1 | Product description and data sheets
0.2 | Installation instructions
0.3 | Connection plans
0.4 | Commissioning instructions
0.5 | Operating instructions
0.6 | Maintenance instructions
0.7 | Error sources, error diagnosis and troubleshooting instructions
1 | PHOTOVOLTAIC SOLAR MODULES - TOTAL POWER 82 kWp |  | 1
1.1 | Mono/polycrystalline solar modules, power of single module > 295 Wp |  | 280
1.2 | Module description: technical specifications - Document which certifies that the modules production process is subject to a permanent quality control
1.3 | Weather resistant Junction box with 3 Bypass-diodes on the backside of the modules with protection class IP 67
1.4 | Wiring of the modules with pin-and-socket connector according to EN 50521 or equivalent
1.5 | Temperature coefficient Pmpp: | <-0,43 %/°C
1.6 | Temperature coefficient Voc: | <-0,33%/°C
1.7 | Temperature coefficient Isc: | >0.02 %/°C
1.8 | Operating temperature range: | -40…+85°C
1.9 | NOCT | 45°C (+/- 2°C)
1.10 | Module efficiency | > 14.0%
1.11 | Positive power sorting
1.12 | Min. 10 year product warranty
1.13 | 25 years linear performance guarantee for the PV modules, such that in year one the guaranteed output power is at least 97% of the nominal power and in year 25 equal or above 80%.
1.14 | CE- conformity, TUV quality certification
1.15 | Horizontal and vertical assembly possible
1.16 | Max. system voltage 1000V
1.17 | Mechanical load (acc. IEC 61215 (5400Pa superimposed load and 2400Pa suction load))
1.18 | Pre-cabled with solar connectors (min. IP 65), connector type: locable, weather proof, plug and play connector
1.19 | Nominal power min. 295 Wp at IEC-Conditions (radiation 1000W/m²,Air-Mass 1.5, 25°C)
1.20 | Nominal ground coverage>134 Wp/m2 at IEC-conditions
1.21 | Product certification | IEC 61215 (Ed.2)
1.22 | Protection class II/ IEC 61730
1.23 | Documentation: | English - French
1.24 | Test standards according to: IEC 61215 (crystalline silicon performance)
2 | SOLAR MOUNTING SYSTEM for 82 kWp Solar Plant - Greenfield racking system |  | 1
2.1 | Greenfield mounting system for framed PV modules (floor mounting system)
2.2 | Module format: | 4 modules horizontally one above the other, 12 module side by side per table
2.3 | Rear and front post aluminium bolted to steel sigma profiles | Connecting elements, solar panel clamps (fasteners)
2.4 | Material: Complete assembly material must be included (stainless steel, aluminium) | Aluminum and stainless steel
2.5 | Mounting inclination angle | 17° to 20°
2.6 | Posts (support): sigma profiles made of galvanised steel for embedding in concrete blocks | Concrete blocks will be produced on site
2.7 | Integrated cable channels (ducts)
2.8 | Product warranty | 10 years
3 | Variable Frequency Drive For Submersible Pump With Selectable Power Supply (PV, Grid, Diesel) |  | 1
3.1 | Input
3.1.1 | Maximum input voltage (Voc) | 800 V-DC
3.1.2 | Minimum input voltage | 400 V-DC
3.1.3 | Recommended voltage DC (VMPP) | 550 - 620 V-DC
3.1.4 | Nominal input voltage AC | 3ph 380 - 480 V 50/60 Hz
3.2 | Output
3.2.1 | Nominal output voltage AC | 3ph 400 V
3.2.2 | Output frequency | 0 - 400 Hz
3.2.3 | Output power | 55 kW / 112 A
3.3 | Efficiency (inverter) | 97 - 98%
3.4 | General information
3.4.1 | Ambient temperature range | -10 - 50° C
3.4.2 | Cooling | natural /by means of internaö
3.4.3 | EMC filter / Motor output | built in
3.4.3.1 |  | EMC-filter for PV inverter 1200 V-DC , max 150 A
3.4.3.2 |  | Output motor filter DV/DT Filter 3 x 500 V-AC
3.4.4 | MPPT function ((Maximum Power Point Tracking)
3.4.5 | Start criteria selectable by system conditions and time
3.4.6 | Stop criteria selectable by frequency or power
3.4.7 | Dry pump detection function
3.4.8 | Low power function
3.4.9 | Compatible with asynchronous and permanent magnets synchronous motors
3.4.10 | Detection of sudden changes of conditions (especially irradiance)
3.4.11 | Two sets of PID gains, for a fast and smooth operation
3.4.12 | Degree of protection | IP54
| Dimension [W x H x D] | 800 x 1800 x 600
Cabinet filter
3.4.13 | Cabinet solution selectable | fuses, ground fault detection
3.5 | Certification | CE; UL
3.6 | Warranty | 3 years
3.7 | Documentation | English
4 | Submersible borehole pump |  | 1
Multistage centrifugal pump for vertical or horizontal installation. Intermediate bearing in every stage. Integerated eays-toremove anti-jam non-return valve. Suction strainer, drive lantern and valve body made of investment casting. Pre-filled submersible motor. Three-phase squirrel cage motor with self-aligning thrust bearing and adequately sized expansion diaphragm for pressure equalisation. Design in compliance with VDE standards.
4.1 | General information
4.1.1 | Pumped medium | Water, Clean water
4.1.2 | Max. fluid temperature | 20.0 °C
4.1.3 | Temperature limit for selected material max. | 50.0 °C
4.1.4 | Density | 998 kg/m³
4.1.5 | Viscosity | 1.00 mm²/s
4.1.6 | Dev. head with non-return valve | 62.67 m
4.1.7 | Flow velocity around motor | 0.2 m/s
4.1.8 | Actual flow rate | 250.00 m³/h
4.1.9 | Actual developed head | 65.24 m
4.1.10 | Power absorbed | 53.70 kW
4.1.11 | Max. power on curve | 53.82 kW
4.1.12 | Min. allowable flow rate | 94.63 m³/h
4.1.13 | Shutoff head | 95.30 m
4.1.14 | Max. allow. flow rate | 317.02 m³/h
4.1.15 | nstallation type | Close-coupled
4.1.16 | Stage number | 3
4.1.17 | Flange connection | Round flange
4.1.18 | Discharge flange nominal pressure | PN 16
4.1.19 | Discharge nominal dia | DN 150
4.1.20 | Non return valve | With
4.1.21 | Valve plate drilled | No
4.1.22 | Bearing pedestal | Without
4.1.23 | Max. outside diameter | 285.0 mm
4.1.24 | Total length of unit | 2479.0 mm
4.1.25 | Frequency invertor | Yes
4.1.26 | Motor speed | 2928 rpm
4.1.27 | Frequency | 50 Hz
4.1.28 | Operating voltage | 400 V
4.1.29 | Rated input P1 | 63.78 kW
4.1.30 | Rated power P2 | 56.00 kW
4.1.31 | Rated current max. | 113.4 A
4.1.32 | Speed | 2931 rpm
4.1.33 | Motor pole number | 2
4.1.34 | Motor enclosure | IP68
4.1.35 | Cos phi at 4/4 load | 0.81
4.1.36 | Motor starting mode | Direct-on-line starting
4.1.37 | Type of current | Three phase (3~)
4.1.38 | Motor efficiency | 87.8 %
4.2 | Material properties
4.2.1 | Suction casing | 1.4517
4.2.2 | Stage casing | 1.4517
4.2.3 | Pump shaft | 1.4462
4.2.5 | Clockwise impeller | 1.4517
4.2.6 | Casing wear ring | 1.4138
4.2.7 | Impeller wear ring | 1.4462
4.2.8 | Bearing sleeve | SiSiC
4.2.9 | Bearing bush | SiSiC
4.2.10 | Valve body | 1.4517
4.2.11 | Stator | 1.4571
4.2.12 | Motor shaft | 1.4460
4.2.13 | Motor cable | Cu- Rubber
4.3 | Warranty | 3 years
4.4 | Documentation | English
5 | ACCESSORIES
5.1 | PV Connection cabinet (fully assembled) for 15 PV-strings with integrated string fuses and two-pole disconnect switches (1000 V) and overvoltage protection SPD Typ II 1000 V-DC |  | 1
5.2 | Degree of protection | IP54
5.4 | Certification | CE; UL
5.5 | Warranty | 3 years
5.6 | Documentation | English
6 | SOLAR CABLE
6.1 | 1 x 6mm², fine copper cable | TÜV Approval Nr. TÜV 2 PfG 1169/08.2007 or equivalent Ozone Resistant according to EN 50396 or equivalent Flame Retardant according to IEC/EN 60332-1-2 or equivalent UV Resistant according to HD 605/A1 or equivalent Halogen Free according to EN 50267-2-1, EN 60684-2 or equivalent Cold Resistant according to IEC/EN 60811-1-4 or equivalent Low Smoke according to IEC/EN 61034 or equivalent Acid and Alkaline Resistant according to IEC/EN 60811-2-1 or equivalent Low Corrosivity of gases according to EN 50267-2-2 or equivalent Weather Resistant according to HD 605/A1 or equivalent Low toxicity of gases according to EN 50267-2-1 or equivalent | 1500 m
7 | SOLAR CABLE CONNECTORS set (m/f) |  | 50
7.1 | Solar Connector, 4-6mm², min 30A/1000V, Spring Closure Construction (tool free crimping) polarity: Minus |  | 25
7.2 | Solar Connector, 4-6mm², min 30A/1000V, Spring Closure Construction (tool free crimping) polarity: Plus |  | 25
8 | Installation material
8.1 | Grounding rods, galvanized steel, 1,50 m; with cable connector |  | 2
8.2 | Solar wire management (solar cable clips) | Button head mounts with cable ties (UV-resistant) | 600
8.3 | Cable ties (black), outdoor use (UV-resistant!) | 4,6 x 300 mm | 500
8.4 | Cable ties (black), outdoor use (UV-resistant!) | 7,6 x 460 mm | 500
8.5 | Equipontential bonding rail |  | 1
9. | Installation according to local and international norms and codes | 1
9.1 | Installation of the complete system under local conditions
9.2 | Connection and embedding to the local infrastructure
10. | Documentation of the entire system | 1
10.1 | Network wiring diagram for the monitoring system
10.2 | Product descriptions and datasheets for all equipment
10.3 | Single-Line Diagram for the complete system
10.4 | Product manufacturer warranties
10.5 | Installation guide in English
10.6 | User manual in English
10.7 | Service notes in English
10.8 | Fault analysis and troubleshooting in English
10.9 | Data sheets for all components in Englisch
11. | General Confirmations & Documentation | 1
11.1 | At least three years experience with the delivery and installation of goods similar to the requested system
11.2 | At least three contracts of a size comparable to the present contract during the last three years
11.3 | Annual tunrnover not less than EURO 1.5 million/annum for PV-Systems during the last three years
11.4 | ISO 9001 certification of the vendor
11.5 | Site survey
11.6 | System to install will perform according to the required output and system components are ensured to function togehter
11.7 | Scope of supply contains all material for the installation and commissioning of the system
11.8 | Local Partner: specify adress + references; licensed with District Electricity Co.
12. | Transport | 1
12.1 | Incoterm 2010 - DDP Balat / Dakhla - Egypt | 25°33'45.29" - 29°15' 51.48"